| Property: | Intracoastal Condominium |  | Address: | 1505 N Riverside Drive. Pompano Beach, FL 33062 |
| --- | --- | --- | --- | --- |
| Permit #: | 25-00001607 |  | Project: | Roofing Project |
| Owner: | Intracoastal Tower Condominium Association |  | Contractor: | Best Roofing |
| Inspection Date: |  | 04/02/2025 |  |  |  |
| Applicable RFI: |  | N/A |  |  |  |
| Component Inspected: |  | Roof |  |  |  |
| Contractor’s Representative(s): |  | Justin Croyle |  |  |  |
| Inspector(s): |  | Jholyn Gutierrez |  |  |  |
| Pending Work: |  | NA |  |  |  |

| Field Conditions: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Weather: | Clear | ☐ | Cloudy | ☐ | Overcast | ☐ |  | Temperature: | 82° |
|  | Sunny | ☒ | Windy | ☐ | Rainy | ☐ |  | Time of Day: | AM |
|  | Humid | ☐ | Foggy | ☐ | Lightning | ☐ |  |  |  |

- Precast Concrete Unit Inspection

| Location: | N/A |
| --- | --- |
| Inspection Outcome: | N/A |
| Comments: | N/A |

- Reinforced Masonry Unit Inspections

| Location: | N/A |
| --- | --- |
| Concrete Mix Design: | N/A |
| Concrete Strength: | N/A |

- Miscellaneous

| Location: | LR- R2, R3, R4 -NORTH WALL |
| --- | --- |
| Inspection Outcome: | In-Progress |
| Comments: | Marcon inspected repairs to the north side knee wall. Areas were approved for either installation of additional rebar and/or cleaning and coating of existing rebar with Sika Armatec 1C per specifications. |

| Location: | LR-STK04 |
| --- | --- |
| Inspection Outcome: | In-Progress |
| Comments: | All stands for AC stack 04 were inspected for compliance with design. Overhangs exceeded 12” maximum per EE drawings. Best Roofing was directed to cut beams to meet acceptable overhang lengths. |

| Inspected By: | Jholyn Gutierrez |  | STAMP HERE |
| --- | --- | --- | --- |
| Approved By: | Charles S. Long, PE |  |  |
| Date Approved: |  |  |  |

| Representative Photos: |  |
| --- | --- |
| - Demolition of knee wall down to rebar. Repair was approved for installation of additional rebar. | - Demolition of knee wall. Repair was approved for cleaning and coating of rebar with Sika Armatec 1C. |
| - Verifying beam dimensions for compliance with approved drawings. Example of non-compliant rail overhang. | - Stand base plates measured for compliance with Engineering Express detail 7B. |