| Property: | Intracoastal Condominium |  | Address: | 1505 N Riverside Drive. Pompano Beach, FL 33062 |
| --- | --- | --- | --- | --- |
| Permit #: | 25-00001607 |  | Project: | Roofing Project |
| Owner: | Intracoastal Tower Condominium Association |  | Contractor: | Best Roofing |
| Inspection Date: |  | 04/7/2025 |  |  |  |
| Applicable RFI: |  | N/A |  |  |  |
| Component Inspected: |  | Roof |  |  |  |
| Contractor’s Representative(s): |  | Justin Croyle |  |  |  |
| Inspector(s): |  | Jholyn Gutierrez |  |  |  |
| Pending Work: |  | NA |  |  |  |

| Field Conditions: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Weather: | Clear | ☐ | Cloudy | ☒ | Overcast | ☐ |  | Temperature: | 82° |
|  | Sunny | ☒ | Windy | ☐ | Rainy | ☐ |  | Time of Day: | AM |
|  | Humid | ☐ | Foggy | ☐ | Lightning | ☐ |  |  |  |

- Precast Concrete Unit Inspection

| Location: | N/A |
| --- | --- |
| Inspection Outcome: | N/A |
| Comments: | N/A |

- Reinforced Masonry Unit Inspections

| Location: | N/A |
| --- | --- |
| Concrete Mix Design: | N/A |
| Concrete Strength: | N/A |

- Miscellaneous

| Location: | LR-STK03 |
| --- | --- |
| Inspection Outcome: | In-Progress |
| Comments: | Marcon observed the application of required OlyBond 500 adhesive along with the installation of the Flat Polyiso foam. All materials complied with GAF specifications. |
| Location: | LR-R1-TOS |
| Inspection Outcome: | In-Progress |
| Comments: | Marcon observed Best roofing chip off the structural roof slab for repairs in accordance with EORs specifications. Steel rebar was cleaned and inspected by Marcon for any signs of corrosion. None were observed. Opened locations were approved for application of concrete. |

| Inspected By: | Jholyn Gutierrez |  | STAMP HERE |
| --- | --- | --- | --- |
| Approved By: | Charles S. Long, PE |  |  |
| Date Approved: |  |  |  |

| Representative Photos: |  |
| --- | --- |
| - Tear off down to the existing concrete deck. Deck surface was dry, clean, and sounded. Rebar was inspected for rusting. | - Application of flashing at all AC stands and other joints. All flashing material and work was in compliance with GAF Specifications |
| - Installation of Cindu polyester membrane 3.5 PLy Polyiso. All material and work complied with GAF specification. | - Application and installation of OlyBond 500 and Flat Polyiso with GRF Facers. All material complied with GAF specification. |